{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":42,"n_cols":9,"rows_kept":42,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","AZAS-MV1"]
[]
[]
[]
[]
["","","","","","AZAS71M2V1B","AZAS100M7V1B","AZAS125M7V1B","AZAS140M7V1B"]
["Dimenzije","Uređaj","","Visina","mm","770","990","990","990"]
["","","","Širina","mm","900","940","940","940"]
["","","","Dubina","mm","320","320","320","320"]
["Težina","Uređaj","","","kg","60","70","70","78"]
["Kompresor","Tip","","","","Hermetički zabrtvljen kompresor s klatnom","Hermetički zabrtvljen kompresor s klatnom","Hermetički zabrtvljen kompresor s klatnom","Hermetički zabrtvljen kompresor s klatnom"]
["Raspon rada","Hlađenje","Ambijent:","Min.","°CDB","-5","-5","-5","-5"]
["","","","Maks.","°CDB","46","46","46","46"]
["","Grijanje","Ambijent:","Min.","°CWB","-15","-15","-15","-15"]
["","","","Maks.","°CWB","15.5","15.5","15.5","15.5"]
["Zvučna snaga","Hlađenje","","","dBA","65","70","71","73"]
["","Grijanje","","","dBA","","","71 (1)","73 (1)"]
["Razina tlaka zvuka","Hlađenje","","Nom.","dBA","46","53","53","54"]
["","Grijanje","","Nom.","dBA","47","57","57","57"]
["Radna tvar","Tip","","","","R-32","R-32","R-32","R-32"]
["","Punjenje","","","kg","2.45","2.60","2.60","2.90"]
["","GWP","","","","675","675","675","675"]
["","Punjenje","","","tCO2Eq","1.65","1.76","1.76","1.96"]
["Priključci cjevovoda","Tekućina","","VP","mm","9.52","9.52","9.52","9.52"]
["","Plin","","VP","mm","15.9","15.9","15.9","15.9"]
["Priključci cjevovoda ","Duljina cjevovoda ","Maks. ","OU - IU","m","30","30","30","30"]
["","","Sistem ","Ekvivalent","m","50","50","50","50"]
["","","","Ne puni se","m","30","30","30","30"]
["Priključci cjevovoda","Punjenje dodatne radne tvari","","","kg/m","Pogledajte priručnik za instalaciju","Pogledajte priručnik za instalaciju","Pogledajte priručnik za instalaciju","Pogledajte priručnik za instalaciju"]
["","Razlika razine","IU - OU","Maks.","m","30.0","30.0","30.0","30.0"]
["","","IU - IU","Maks.","m","0.5","0.5","0.5","0.5"]
["Standardna dodatna oprema","Installation manual","","","","1","1","1","1"]
["","Refrigerant label for F-gas regulation","","","","1","1","1","1"]
["","General safety precautions","","","","1","1","1","1"]
["","LOT10 Energy Label","","","","1","1","1","1"]
["","Tie-wraps","","","","2","2","2","2"]
["Napajanje","Faza","","","","1~","1~","1~","1~"]
["","Frekvencija","","","Hz","50","50","50","50"]
["","Napon","","","V","220-240","220-240","220-240","220-240"]
["Struja - 50 Hz","Preporučeni osigurač (MFA)","","","A","20","25","32","32"]
["Standardna dodatna oprema","Peel off F-gas label","","","","1"]
["Napomene","","","","","","","(1) - U skladu s ENER serija 21","(1) - U skladu s ENER serija 21"]